## Sheet1
project_no | tag_no | flow_sheet_no | A3 | A4 | line_size | line_class | B3 | B4 | fluid_phase | flowing_fluid | C3 | C4 | max_flow_rate | norm_flow_rate | min_flow_rate | flow_rate_unit | upstream_pressure | D2 | D3 | upstream_pressure_unit | oper_diff_press max | oper_diff_press nor | oper_diff_press min | oper_diff_press_unit | Design_Pres_For_Actuator | Design_Pres_For_Actuator_unit | Max_Diff_Pres_For_Actuator | Max_Diff_Pres_For_Actuator_unit | norm_oper | mechanical_design_temp | G3 | norm_oper_unit | visc_at_t | H2 | H3 | visc_at_t_unit | solids | I2 | I3 | solids_unit | m_w | z | cp_cv | sp_gr_at_t | vapor_press_pv | critical_press_pc | K3 | vapor_press_pv_unit | flash | flash_unit | sup_heat_temp | sup_heat_temp_unit | tso | valve_failure_code | M3 | M4 | rev_no | remarks
12E0966A | LV-6060 | PA-16105 |  |  | 3 | A21D1 |  |  | LIQUID | CONDENSATE |  |  | - | 20 | - | m3/hr | - | 3.7 | - | kg/cm2 g | - | 3.3 | - | kg/cm2 | 10.5 | kg/cm2 g | 10.5 | kg/cm2 | 45 | 200 |  | ℃ | 0.55 |  |  | cP |  |  |  | % | - | - | - | 0.99 | 0.1 | 225 |  | kg/cm2 a | - | % | - | ℃ | - | FO |  |  | 1A
12E0966A | TV-6044 | PA-16100 |  |  | 1-1/2 | A21X |  |  | STEAM | MP STEAM |  |  | 86.9 | 57.2 | - | kg/hr | 9 | 9 | - | kg/cm2 g | 0.7 | 0.7 | - | kg/cm2 | 12 | kg/cm2 g | 12 | kg/cm2 | 202 | 250 |  | ℃ | 0.02 |  |  | cP |  |  |  | % | 18 | 1 | 1.4 | - | - | - |  | kg/cm2 a | - | % | 22 | ℃ | - | FC |  |  | 1A
12E0966A | TV-6062 | PA-16105 |  |  | 4 | A21A |  |  | LIQUID | TEMPERED WATER |  |  | 105.6 | 81.2 | - | m3/hr | 3.396 | 4.232 | - | kg/cm2 g | 0.119 | 1.205 | - | kg/cm2 | 6.2 | kg/cm2 g | 6.2 | kg/cm2 | 15.8 | 200 |  | ℃ | 1.1 |  |  | cP |  |  |  | % | - | - | - | 1 | 0.018 | 225 |  | kg/cm2 a | - | % |  | ℃ | - | - |  |  | 1A | 3-Way Valve. Fail position from A to C
12E0966A | TV-6070 | PA-16200 |  |  | 2 | A21X |  |  | STEAM | MP STEAM |  |  | 82.1 | 68.4 | - | kg/hr | 9 | 9 | - | kg/cm2 g | 0.7 | 0.7 | - | kg/cm2 | 12 | kg/cm2 g | 12 | kg/cm2 | 202 | 250 |  | ℃ | 0.02 |  |  | cP |  |  |  | % | 18 | 1 | 1.4 | - | - | - |  | kg/cm2 a | - | % | 22 | ℃ | - | FC |  |  | 1A
12E0966A | XV-6308 | PA-16105 |  |  | 2 | A21X |  |  | LIQUID | CONDENSATE |  |  | - | - | - | m3/hr | - | 4.7 | - | kg/cm2 g | - | MIN. | - | kg/cm2 | 10.5 | kg/cm2 g | 10.5 | kg/cm2 | 45 | 200 |  | ℃ | 0.238 |  |  | cP |  |  |  | % | - | - | - | 0.99 | 2 | 225 |  | kg/cm2 a | - | % | - | ℃ | - | FC |  |  | 1A | On/Off Valve Line Size Valve